## Water Treatment Chem Cost Sheet
Chemical | Unit of Measure (UOM) | Unit Cost | LRWRA Shipping Costs (based on full truckload) | LRWRA Delivered Cost | National Freight Charge per UOM mile* (based on full truckload)
Activated Carbon: In 50 lb bags. Price is per lb | Pounds
Activated Carbon: In 1,5000 lb supersacks. Price is per lb | Pounds
Aluminum Sulfate (Alum): Delivered via bulk tanker truck. Price is per gallon. | Gallons
Aluminum Sulfate (Alum): In 275 gallon tote. Price is per gallon. | Gallons
Aqua Ammonia: Delivered via bulk tanker truck. Price is per gallon. | Gallons
Aqua Ammonia: In 275 gallon tote. Price is per gallon. | Gallons
Calcium Hypochlorite: In 100 lb drums (or smaller). Price is per lb. | Pounds
Calcium Nitrate: Delivered via bulk tanker truck. Price is per gallon. | Gallons
Calcium Nitrate: In 275 gallon tote. Price is per gallon. | Gallons
Chlorine Gas: In 150 lb cylinders. Price is per lb. | Pounds
Chlorine Gas: In 1 ton containers. Price is per lb. | Pounds
Ferric Chloride: Delivered via bulk tanker truck. Price is per gallon. | Gallons
Ferric Chloride: In 275 gallon tote. Price is per gallon. | Gallons
Ferric Sulfate: Delivered via bulk tanker truck. Price is per gallon. | Gallons
Ferric Sulfate: In 275 gallon tote. Price is per gallon. | Gallons
Ferrous Chloride: Delivered via bulk tanker truck. Price is per gallon. | Gallons
Ferrous Chloride: Delivered in totes. Price is per gallon. | Gallons
Hydrated Lime: In 50 lb bags. Price is per pound. | Pounds
Hydrated Lime: In 1,000 lb supersacks. Price is per lb. | Pounds
Liquid Caustic Soda (Sodium Hydroxide): Delivered via bulk tanker truck. Price is per gallon. | Gallons
Liquid Caustic Soda (Sodium Hydroxide): In 330 gallon tote. Price is per gallon. | Gallons
Liquid Chlorine: In pressurize cylinder. Price is per lb. | Pounds
Liquid Chlorine: In pressurize 1 ton container. Price is per lb. | Pounds
Liquid Lime: Delivered via agitated tanker truck. Price is per gallon. | Gallons
Liquid Lime: Delivered via tote. Price is per gallon. | Gallons
Magnesium Hydroxide: Delivered via agitated tanker truck. Price is per gallon. | Gallons
Magnesium Hydroxide: Delivered via tote. Price is per gallon. | Gallons
Peracetic Acid (PAA): In 55 gallon drum. Price is per gallon. | Gallons
Peracetic Acid (PAA): In 330 gallon tote. Price is per gallon. | Gallons
Phosphoric Acid / Orthophosphate Blends: Delivered via bulk tanker truck. Price is per gallon. | Gallons
Phosphoric Acid / Orthophosphate Blends: In 275 gallon tote. Price is per gallon. | Gallons
Polyaluminum Chloride (PAC): Delivered via bulk tanker truck. Price is per gallon. | Gallons
Polyaluminum Chloride (PAC): In 275 gallon tote. Price is per gallon. | Gallons
Potassium Permanganate: In 55 gallon pails. Price is per gallon. | Gallons
Potassium Permanganate: In 100 gallon drums. Price is per gallon. | Gallons
Sodium Bisulfite: Delivered via bulk tanker truck. Price is per gallon. | Gallons
Sodium Bisulfite: In 275 gallon tote. Price is per gallon. | Gallons
Sodium Bisulfite: In 55 gallon pails. Price is per gallon. | Gallons
Sodium Hypochlorite: Delivered via bulk tanker truck. Price is per gallon. | Gallons
Sodium Hypochlorite: In 275 gallon tote. Price is per gallon. | Gallons
Sulfur Dioxide (Liquid): In 1 ton containers. Price is per lb. | Pounds
Sulfur Dioxide (Liquid): In 150 lb cylinder. Price is per lb. | Pounds
*Charge per UoM mile shall be established as distance from vendors closest distribution facility.

## Polymer Cost Sheet
Chemical | Product | UOM | Raw Material Cost | Blending Lab Costs | LRWRA Shipping Costs | National Freight Charge per UOM mile
Polymer Flocculants (e.g., Polyacrylamide) In 50 lb bags |  | Pound
Polymer Flocculants (e.g., Polyacrylamide) In 1,200 lb bags |  | Pound
Polymer Flocculants (e.g., Polyacrylamide) In 1,650 lb bags |  | Pound
Polymer Flocculants (e.g., Polyacrylamide) In 2,400 lb bags |  | Pound

## Chemicals List & Specifications
Chemical | AWWA/NSF Standard | Minimum Purity / Composition | Packaging & Delivery Format | Required Documentation | Shelf Life & Testing | Logistics & Safety Requirements
Activated Carbon | NSF/ANSI 61 | Iodine number ≥ 800 mg/g; Moisture ≤ 5%; Ash ≤ 15% | 50 lb bags or 1,000 lb supersacks, shrink-wrapped on pallets; dry granular or powdered form | Certificate of Analysis (COA), SDS, origin and treatment process documentation, NSF certification | 12 months from production; COA required per batch; iodine number verification required | Delivered on pallets; forklift unload; moisture-resistant packaging; spill control during transfer
Aluminum Sulfate (Alum) | AWWA B403-21, NSF/ANSI 60 | ≥ 8.0% Al₂O₃ (48.5% solution), free acid ≤ 0.5%, specific gravity ≥ 1.33 | Bulk tankers or 275-gallon totes with closed-loop fittings; liquid form | COA, SDS, NSF certificate, pH and Al₂O₃ assay | 30 days from manufacture; COA per delivery required | DOT placarded tankers; corrosion-resistant fittings; spill containment during offload
Aqua Ammonia | AWWA B302, NSF/ANSI 60 | 19–30% NH₃ by weight; clear, colorless, and sediment-free | Bulk tankers or 275-gallon totes with pressure/vapor recovery fittings | COA, SDS, ammonia concentration certificate, NSF certification | 30 days max; batch-specific COA required | DOT-compliant delivery; spill containment and vapor control systems mandatory
Calcium Hypochlorite | AWWA B300-21, NSF/ANSI 60 | ≥ 65% available chlorine; Moisture ≤ 10% | 100-lb drums or smaller UN-rated containers; granular or tablet form | COA, SDS, packaging certificate, NSF documentation | 12 months from manufacture; lot testing required for chlorine content | Stored dry; oxidizer placard; keep away from organic materials
Chlorine Gas | AWWA B301-20 | ≥ 99.5% Cl₂; Free moisture ≤ 0.02% | 150-lb cylinders or 1-ton containers; pressurized gas | COA, SDS, valve inspection report, DOT and CGA compliance | 24 months; cylinder integrity inspections required | HAZMAT transport only; valve guards mandatory; 24/7 spill response required
Ferric Chloride | AWWA B407-18, NSF/ANSI 60 | ≥ 37% Fe³⁺ by weight; Free acid ≤ 0.5%; Specific gravity ≥ 1.40 | Bulk tankers or 275-gallon totes; liquid | COA, SDS, NSF certificate, iron content assay | 60 days; COA per delivery required | Requires corrosion-resistant unloading systems; closed-loop transfer required
Ferric Sulfate | AWWA B406-18, NSF/ANSI 60 | ≥ 12% Fe³⁺; Specific gravity ≥ 1.45 | Bulk liquid tankers or totes; liquid | COA, SDS, NSF certificate | 60 days from manufacture; COA required per batch | Tank trailers must be FRP or 316SS; HAZMAT compliant
Ferrous Chloride | NSF/ANSI 60 | ≥ 30% Fe²⁺ by weight; Specific gravity ≥ 1.20; stabilized to prevent oxidation | Bulk liquid form in lined tankers or totes; corrosion-resistant valves required | COA, SDS, NSF certification, pH and iron content analysis | 60 days; COA per batch required | Delivered with corrosion-resistant fittings; HAZMAT-compliant transport; spill control required
Hydrated Lime | AWWA B202-19, NSF/ANSI 60 | ≥ 85% Ca(OH)₂; Moisture ≤ 2%; Free of lumps > 0.5 mm | 50 lb bags, supersacks, or pneumatic tankers; dry powder | COA, SDS, sieve analysis, lime index | 6 months; COA with fineness and purity per shipment | Dust control required; offload by blower or forklift; waterproof storage area
Liquid Caustic Soda (Sodium Hydroxide) | AWWA B501-20, NSF/ANSI 60 | ≥ 25% or 50% NaOH; Iron ≤ 5 ppm; Mercury/Nickel ≤ 0.1 ppm | Bulk tankers or 330-gal totes; liquid | COA, SDS, membrane-cell production certification | 90 days; COA per load required | Delivered in insulated tankers; dedicated unloading line; PPE required at offload
Liquid Chlorine | AWWA B301-20, NSF/ANSI 60 | ≥ 99.5% Cl₂; moisture ≤ 0.02% | Pressurized ton containers or cylinders | COA, SDS, DOT cylinder compliance, leak test records | 24 months; certified cylinder testing | HAZMAT shipping; protective valve guards; emergency venting plan
Liquid Lime | ASTM C977, NSF/ANSI 60 | ≥ 30% Ca(OH)₂ solids; suspended uniformly; pH ≥ 12.4 | Agitated tankers or totes; pumpable slurry | COA, SDS, solids certification, NSF listing | 30 days max; particle size test per load | Agitated delivery trucks; storage tanks must have mechanical mixers
Magnesium Hydroxide | NSF/ANSI 60 | ≥ 95% Mg(OH)₂; minimum 60% solids; grit-free suspension | Agitated tankers or IBC totes; pumpable slurry | COA, SDS, solids content certificate, NSF compliance | 30 days; stability test and COA per load | Agitated delivery system required; storage must include mixing equipment; HAZMAT-compliant handling
Phosphoric Acid / Orthophosphate Blends | AWWA B502-18, NSF/ANSI 60 | ≥ 75% H₃PO₄; ortho:poly blend ratio required; heavy metals ≤ 10 ppb | Bulk tankers or 275-gallon totes; liquid | COA, SDS, blend composition, NSF proof | 60 days; phosphate assay and stability testing required | Corrosion-resistant hoses; spill containment; temperature-controlled storage
Polyaluminum Chloride (PAC) | NSF/ANSI 60 | Al₂O₃ ≥ 10%; basicity 50–70%; pH 2.5–4.5 | Bulk tankers or 275-gallon totes; liquid | COA, SDS, NSF certificate, aluminum content assay, basicity report | 60 days; stability report and COA with delivery | DOT-compliant liquid handling; closed-loop unloading; corrosion-resistant delivery connections
Polymer Flocculants (e.g., Polyacrylamide) | NSF/ANSI 60 | Active polymer ≥ 90%; residual monomer ≤ 0.05% | Emulsion (oil based), dry (powder), or solution; 55-gallon drums, 275-gallon totes, 50 lb bags, supersack | COA, SDS, charge density and molecular weight data, NSF certification | 12 months (emulsion); 24 months (dry); COA required with each shipment | Temperature-controlled storage (40–90°F); avoid freezing; labeled hazardous if emulsified
Potassium Permanganate | AWWA B603-17, NSF/ANSI 60 | ≥ 97% KMnO₄; Insoluble matter ≤ 0.1% | 55-lb pails or 100-lb drums; dry crystalline form | COA, SDS, lot analysis, NSF listing | 12 months; KMnO₄ assay required per batch | Oxidizer placard required; protect from moisture; UN-approved containers
Sodium Bisulfite | NSF/ANSI 60 | ≥ 38% NaHSO₃; Iron ≤ 0.1 ppm | Bulk tankers, 55-gallon drums, or 275-gallon totes; liquid | COA, SDS, heavy metals screening, NSF certification | 30 days; test for bisulfite stability per shipment | Ventilated delivery; dedicated lines; DOT-compliant placards
Sodium Hypochlorite | AWWA B300-21, NSF/ANSI 60 | 12.5–15% available chlorine; iron ≤ 0.5 ppm; free alkali ≥ 0.15% | Bulk delivery or 275-gallon totes; liquid | COA, SDS, date of manufacture, NSF proof | 21 days max from production; decomposition rate required | UV-protected containers; vented totes; refillable tote return program recommended
Sulfur Dioxide (Liquid) | AWWA B609-19 | ≥ 99.9% SO₂; Non-condensable gases ≤ 0.05% | 1-ton DOT-certified containers or 150-lb cylinders | COA, SDS, DOT compliance, cylinder pressure inspection | 24 months; valve and seal certification required | HAZMAT-certified carriers; corrosion-resistant handling; 24/7 spill hotline
Calcium Nitrate | NSF/ANSI 60 | 70–76% Ca(NO₃)₂ by weight; clear, colorless solution | Bulk tankers or 275-gallon totes | COA, SDS, nitrate concentration assay, NSF certification | 60 days from manufacture; COA required with each shipment | DOT-compliant delivery; spill containment equipment required; must prevent exposure to moisture
Peracetic Acid (PAA) | ASTM/EPA specifications, NSF/ANSI 60 | ≥15% peracetic acid with stabilizers; includes hydrogen peroxide and acetic acid | 55-gallon drums or 330-gallon totes; temperature-controlled | COA, SDS, PAA concentration assay, NSF certification | 60 days from manufacture; stability data and COA required for each delivery | Ventilated transport; spill kits required onboard; emergency contact line must be available 24/7